## bus
| name | vn_kv | type | zone | in_service | max_vm_pu | min_vm_pu | geo
0 | 1 | 135 | b | 1 | TRUE | 1.06 | 0.94 | "{\"coordinates\": [1.9673949894, -0.9610198739], \"type\": \"Point\"}"
1 | 2 | 135 | b | 1 | TRUE | 1.06 | 0.94 | "{\"coordinates\": [2.9779852289, -1.0412882366], \"type\": \"Point\"}"
2 | 3 | 135 | b | 1 | TRUE | 1.06 | 0.94 | "{\"coordinates\": [3.780660539, -1.6066859687], \"type\": \"Point\"}"
3 | 4 | 135 | b | 1 | TRUE | 1.06 | 0.94 | "{\"coordinates\": [3.8337344898, -0.4914657254], \"type\": \"Point\"}"
4 | 5 | 135 | b | 1 | TRUE | 1.06 | 0.94 | "{\"coordinates\": [2.6937067209, -0.095882852], \"type\": \"Point\"}"
5 | 6 | 0.208 | b | 1 | TRUE | 1.06 | 0.94 | "{\"coordinates\": [2.5321180205, 1.2056156419], \"type\": \"Point\"}"
6 | 7 | 14 | b | 1 | TRUE | 1.06 | 0.94 | "{\"coordinates\": [4.8721406581, -0.2692952825], \"type\": \"Point\"}"
7 | 8 | 12 | b | 1 | TRUE | 1.06 | 0.94 | "{\"coordinates\": [5.9042747731, -0.5402149495], \"type\": \"Point\"}"
8 | 9 | 0.208 | b | 1 | TRUE | 1.06 | 0.94 | "{\"coordinates\": [4.274948799, 0.5335379916], \"type\": \"Point\"}"
9 | 10 | 0.208 | b | 1 | TRUE | 1.06 | 0.94 | "{\"coordinates\": [3.2723067024, 0.9619849305], \"type\": \"Point\"}"
10 | 11 | 0.208 | b | 1 | TRUE | 1.06 | 0.94 | "{\"coordinates\": [1.8366837619, 1.0890065149], \"type\": \"Point\"}"
11 | 12 | 0.208 | b | 1 | TRUE | 1.06 | 0.94 | "{\"coordinates\": [2.3371166416, 2.3091630377], \"type\": \"Point\"}"
12 | 13 | 0.208 | b | 1 | TRUE | 1.06 | 0.94 | "{\"coordinates\": [3.3094922817, 2.1179802998], \"type\": \"Point\"}"
13 | 14 | 0.208 | b | 1 | TRUE | 1.06 | 0.94 | "{\"coordinates\": [4.3962052866, 1.6847581464], \"type\": \"Point\"}"

## load
| name | bus | p_mw | q_mvar | const_z_p_percent | const_z_q_percent | const_i_p_percent | const_i_q_percent | sn_mva | scaling | in_service | type | controllable
0 |  | 1 | 21.7 | 12.7 | 0 | 0 | 0 | 0 |  | 1 | TRUE |  | FALSE
1 |  | 2 | 94.2 | 19 | 0 | 0 | 0 | 0 |  | 1 | TRUE |  | FALSE
2 |  | 3 | 47.8 | -3.9 | 0 | 0 | 0 | 0 |  | 1 | TRUE |  | FALSE
3 |  | 4 | 7.6 | 1.6 | 0 | 0 | 0 | 0 |  | 1 | TRUE |  | FALSE
4 |  | 5 | 11.2 | 7.5 | 0 | 0 | 0 | 0 |  | 1 | TRUE |  | FALSE
5 |  | 8 | 29.5 | 16.6 | 0 | 0 | 0 | 0 |  | 1 | TRUE |  | FALSE
6 |  | 9 | 9 | 5.8 | 0 | 0 | 0 | 0 |  | 1 | TRUE |  | FALSE
7 |  | 10 | 3.5 | 1.8 | 0 | 0 | 0 | 0 |  | 1 | TRUE |  | FALSE
8 |  | 11 | 6.1 | 1.6 | 0 | 0 | 0 | 0 |  | 1 | TRUE |  | FALSE
9 |  | 12 | 13.5 | 5.8 | 0 | 0 | 0 | 0 |  | 1 | TRUE |  | FALSE

## gen
| name | bus | p_mw | vm_pu | sn_mva | min_q_mvar | max_q_mvar | scaling | slack | in_service | slack_weight | type | controllable | max_p_mw | min_p_mw | id_q_capability_characteristic | reactive_capability_curve | curve_style
0 |  | 1 | 40 | 1.045 |  | -40 | 50 | 1 | FALSE | TRUE | 0 |  | TRUE | 140 | 0 |  | FALSE
1 |  | 2 | 0 | 1.01 |  | 0 | 40 | 1 | FALSE | TRUE | 0 |  | TRUE | 100 | 0 |  | FALSE
2 |  | 5 | 0 | 1.07 |  | -6 | 24 | 1 | FALSE | TRUE | 0 |  | TRUE | 100 | 0 |  | FALSE
3 |  | 7 | 0 | 1.09 |  | -6 | 24 | 1 | FALSE | TRUE | 0 |  | TRUE | 100 | 0 |  | FALSE

## shunt
| bus | name | q_mvar | p_mw | vn_kv | step | max_step | in_service | id_characteristic_table | step_dependency_table
0 | 8 |  | -19 | 0 | 0.208 | 1 | 1 | TRUE |  | FALSE

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service | max_p_mw | min_p_mw | max_q_mvar | min_q_mvar
0 |  | 0 | 1.06 | 0 | 1 | TRUE | 332.4 | 0 | 10 | 0

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service | max_loading_percent | geo
0 |  |  | 0 | 1 | 1 | 3.532 | 10.7837 | 768.4848 | 0 | 42.339 | 1 | 1 | ol | TRUE | 100 | null
1 |  |  | 0 | 4 | 1 | 9.847 | 40.649 | 716.0881 | 0 | 42.339 | 1 | 1 | ol | TRUE | 100 | null
2 |  |  | 1 | 2 | 1 | 8.5639 | 36.08 | 637.4931 | 0 | 42.339 | 1 | 1 | ol | TRUE | 100 | null
3 |  |  | 1 | 3 | 1 | 10.5905 | 32.1343 | 494.8576 | 0 | 42.339 | 1 | 1 | ol | TRUE | 100 | null
4 |  |  | 1 | 4 | 1 | 10.3791 | 31.6896 | 503.5904 | 0 | 42.339 | 1 | 1 | ol | TRUE | 100 | null
5 |  |  | 2 | 3 | 1 | 12.2126 | 31.1702 | 186.2993 | 0 | 42.339 | 1 | 1 | ol | TRUE | 100 | null
6 |  |  | 3 | 4 | 1 | 2.433 | 7.6745 | 0 | 0 | 42.339 | 1 | 1 | ol | TRUE | 100 | null
7 |  |  | 5 | 10 | 1 | 4.1092e-05 | 8.6052e-05 | 0 | 0 | 27479.6522 | 1 | 1 | ol | TRUE | 100 | null
8 |  |  | 5 | 11 | 1 | 5.3176e-05 | 0.00011067 | 0 | 0 | 27479.6522 | 1 | 1 | ol | TRUE | 100 | null
9 |  |  | 5 | 12 | 1 | 2.8619e-05 | 5.636e-05 | 0 | 0 | 27479.6522 | 1 | 1 | ol | TRUE | 100 | null
10 |  |  | 8 | 9 | 1 | 1.3762e-05 | 3.6558e-05 | 0 | 0 | 27479.6522 | 1 | 1 | ol | TRUE | 100 | null
11 |  |  | 8 | 13 | 1 | 5.4993e-05 | 0.00011698 | 0 | 0 | 27479.6522 | 1 | 1 | ol | TRUE | 100 | null
12 |  |  | 9 | 10 | 1 | 3.5498e-05 | 8.3097e-05 | 0 | 0 | 27479.6522 | 1 | 1 | ol | TRUE | 100 | null
13 |  |  | 11 | 12 | 1 | 9.5579e-05 | 8.6476e-05 | 0 | 0 | 27479.6522 | 1 | 1 | ol | TRUE | 100 | null
14 |  |  | 12 | 13 | 1 | 7.3951e-05 | 0.00015057 | 0 | 0 | 27479.6522 | 1 | 1 | ol | TRUE | 100 | null

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | parallel | df | in_service | max_loading_percent | tap_changer_type
0 |  |  | 3 | 6 | 9900 | 135 | 14 | 2070.288 | 0 | 0 | 0 | 0 | hv | 0 |  |  | 2.2 |  | -1 | 1 | 1 | TRUE | 100 | Ratio
1 |  |  | 3 | 8 | 9900 | 135 | 0.208 | 5506.182 | 0 | 0 | 0 | 0 | hv | 0 |  |  | 3.1 |  | -1 | 1 | 1 | TRUE | 100 | Ratio
2 |  |  | 4 | 5 | 9900 | 135 | 0.208 | 2494.998 | 0 | 0 | 0 | 0 | hv | 0 |  |  | 6.8 |  | -1 | 1 | 1 | TRUE | 100 | Ratio
3 |  |  | 6 | 7 | 9900 | 14 | 12 | 1743.885 | 0 | 0 | 0 | 0 | [7 empty] | 1 | 1 | TRUE | 100
4 |  |  | 6 | 8 | 9900 | 14 | 0.208 | 1089.099 | 0 | 0 | 0 | 0 | [7 empty] | 1 | 1 | TRUE | 100

## poly_cost
| element | et | cp0_eur | cp1_eur_per_mw | cp2_eur_per_mw2 | cq0_eur | cq1_eur_per_mvar | cq2_eur_per_mvar2
0 | 0 | ext_grid | 0 | 20 | 0.043029 | 0 | 0 | 0
1 | 0 | gen | 0 | 20 | 0.25 | 0 | 0 | 0
2 | 1 | gen | 0 | 40 | 0.01 | 0 | 0 | 0
3 | 2 | gen | 0 | 40 | 0.01 | 0 | 0 | 0
4 | 3 | gen | 0 | 40 | 0.01 | 0 | 0 | 0

## line_std_types
| type | r_ohm_per_km | q_mm2 | x_ohm_per_km | c_nf_per_km | max_i_ka
NAYY 4x150 SE | cs | 0.208 | 150 | 0.08 | 261 | 0.27
70-AL1/11-ST1A 20.0 | ol | 0.4132 | 70 | 0.36 | 9.7 | 0.29
NA2XS2Y 1x70 RM/25 6/10 kV | cs | 0.443 | 70 | 0.123 | 280 | 0.217
N2XS(FL)2Y 1x300 RM/35 64/110 kV | cs | 0.06 | 300 | 0.144 | 144 | 0.588
NA2XS2Y 1x120 RM/25 6/10 kV | cs | 0.253 | 120 | 0.113 | 340 | 0.28
149-AL1/24-ST1A 10.0 | ol | 0.194 | 149 | 0.315 | 11.25 | 0.47
15-AL1/3-ST1A 0.4 | ol | 1.8769 | 16 | 0.35 | 11 | 0.105
NA2XS2Y 1x185 RM/25 6/10 kV | cs | 0.161 | 185 | 0.11 | 406 | 0.358
NA2XS2Y 1x240 RM/25 6/10 kV | cs | 0.122 | 240 | 0.105 | 456 | 0.416
N2XS(FL)2Y 1x240 RM/35 64/110 kV | cs | 0.075 | 240 | 0.149 | 135 | 0.526
NAYY 4x120 SE | cs | 0.225 | 120 | 0.08 | 264 | 0.242
48-AL1/8-ST1A 10.0 | ol | 0.5939 | 48 | 0.35 | 10.1 | 0.21
94-AL1/15-ST1A 10.0 | ol | 0.306 | 94 | 0.33 | 10.75 | 0.35
NA2XS2Y 1x70 RM/25 12/20 kV | cs | 0.443 | 70 | 0.132 | 190 | 0.22
243-AL1/39-ST1A 20.0 | ol | 0.1188 | 243 | 0.32 | 11 | 0.645
NA2XS2Y 1x150 RM/25 6/10 kV | cs | 0.206 | 150 | 0.11 | 360 | 0.315
184-AL1/30-ST1A 110.0 | ol | 0.1571 | 184 | 0.4 | 8.8 | 0.535
149-AL1/24-ST1A 110.0 | ol | 0.194 | 149 | 0.41 | 8.75 | 0.47
NA2XS2Y 1x240 RM/25 12/20 kV | cs | 0.122 | 240 | 0.112 | 304 | 0.421
122-AL1/20-ST1A 20.0 | ol | 0.2376 | 122 | 0.344 | 10.3 | 0.41
48-AL1/8-ST1A 20.0 | ol | 0.5939 | 48 | 0.372 | 9.5 | 0.21
34-AL1/6-ST1A 10.0 | ol | 0.8342 | 34 | 0.36 | 9.7 | 0.17
24-AL1/4-ST1A 0.4 | ol | 1.2012 | 24 | 0.335 | 11.25 | 0.14
184-AL1/30-ST1A 20.0 | ol | 0.1571 | 184 | 0.33 | 10.75 | 0.535
94-AL1/15-ST1A 20.0 | ol | 0.306 | 94 | 0.35 | 10 | 0.35
NAYY 4x50 SE | cs | 0.642 | 50 | 0.083 | 210 | 0.142
490-AL1/64-ST1A 380.0 | ol | 0.059 | 490 | 0.253 | 11 | 0.96
48-AL1/8-ST1A 0.4 | ol | 0.5939 | 48 | 0.3 | 12.2 | 0.21
NA2XS2Y 1x95 RM/25 6/10 kV | cs | 0.313 | 95 | 0.123 | 315 | 0.249
NA2XS2Y 1x120 RM/25 12/20 kV | cs | 0.253 | 120 | 0.119 | 230 | 0.283
34-AL1/6-ST1A 20.0 | ol | 0.8342 | 34 | 0.382 | 9.15 | 0.17
94-AL1/15-ST1A 0.4 | ol | 0.306 | 94 | 0.29 | 13.2 | 0.35
NA2XS2Y 1x185 RM/25 12/20 kV | cs | 0.161 | 185 | 0.117 | 273 | 0.362
NA2XS2Y 1x150 RM/25 12/20 kV | cs | 0.206 | 150 | 0.116 | 250 | 0.319
243-AL1/39-ST1A 110.0 | ol | 0.1188 | 243 | 0.39 | 9 | 0.645
490-AL1/64-ST1A 220.0 | ol | 0.059 | 490 | 0.285 | 10 | 0.96
N2XS(FL)2Y 1x185 RM/35 64/110 kV | cs | 0.099 | 185 | 0.156 | 125 | 0.457
N2XS(FL)2Y 1x120 RM/35 64/110 kV | cs | 0.153 | 120 | 0.166 | 112 | 0.366
NA2XS2Y 1x95 RM/25 12/20 kV | cs | 0.313 | 95 | 0.132 | 216 | 0.252
122-AL1/20-ST1A 10.0 | ol | 0.2376 | 122 | 0.323 | 11.1 | 0.41
149-AL1/24-ST1A 20.0 | ol | 0.194 | 149 | 0.337 | 10.5 | 0.47
70-AL1/11-ST1A 10.0 | ol | 0.4132 | 70 | 0.339 | 10.4 | 0.29
305-AL1/39-ST1A 110.0 | ol | 0.0949 | 305 | 0.38 | 9.2 | 0.74

## trafo_std_types
| shift_degree | vector_group | vn_hv_kv | pfe_kw | i0_percent | vn_lv_kv | sn_mva | tap_step_degree | tap_neutral | tap_min | vkr_percent | tap_step_percent | tap_side | tap_phase_shifter | tap_max | vk_percent
0.4 MVA 20/0.4 kV | 150 | Dyn5 | 20 | 1.35 | 0.3375 | 0.4 | 0.4 | 0 | 0 | -2 | 1.425 | 2.5 | hv | FALSE | 2 | 6
63 MVA 110/20 kV v1.4.3 and older | 150 | YNd5 | 110 | 33 | 0.086 | 20 | 63 | 0 | 0 | -9 | 0.322 | 1.5 | hv | FALSE | 9 | 11.2
63 MVA 110/10 kV v1.4.3 and older | 150 | YNd5 | 110 | 31.51 | 0.078 | 10 | 63 | 0 | 0 | -9 | 0.31 | 1.5 | hv | FALSE | 9 | 10.04
25 MVA 110/20 kV v1.4.3 and older | 150 | YNd5 | 110 | 29 | 0.071 | 20 | 25 | 0 | 0 | -9 | 0.282 | 1.5 | hv | FALSE | 9 | 11.2
40 MVA 110/20 kV v1.4.3 and older | 150 | YNd5 | 110 | 31 | 0.08 | 20 | 40 | 0 | 0 | -9 | 0.302 | 1.5 | hv | FALSE | 9 | 11.2
0.25 MVA 20/0.4 kV | 150 | Yzn5 | 20 | 0.8 | 0.32 | 0.4 | 0.25 | 0 | 0 | -2 | 1.44 | 2.5 | hv | FALSE | 2 | 6
25 MVA 110/10 kV v1.4.3 and older | 150 | YNd5 | 110 | 28.51 | 0.073 | 10 | 25 | 0 | 0 | -9 | 0.276 | 1.5 | hv | FALSE | 9 | 10.04
0.25 MVA 10/0.4 kV | 150 | Dyn5 | 10 | 0.6 | 0.24 | 0.4 | 0.25 | 0 | 0 | -2 | 1.2 | 2.5 | hv | FALSE | 2 | 4
160 MVA 380/110 kV | 0 | Yy0 | 380 | 60 | 0.06 | 110 | 160 | 0 | 0 | -9 | 0.25 | 1.5 | hv | FALSE | 9 | 12.2
63 MVA 110/10 kV | 150 | YNd5 | 110 | 22 | 0.04 | 10 | 63 | 0 | 0 | -9 | 0.32 | 1.5 | hv | FALSE | 9 | 18
0.63 MVA 20/0.4 kV | 150 | Dyn5 | 20 | 1.65 | 0.2619 | 0.4 | 0.63 | 0 | 0 | -2 | 1.206 | 2.5 | hv | FALSE | 2 | 6
0.4 MVA 10/0.4 kV | 150 | Dyn5 | 10 | 0.95 | 0.2375 | 0.4 | 0.4 | 0 | 0 | -2 | 1.325 | 2.5 | hv | FALSE | 2 | 4
0.63 MVA 10/0.4 kV | 150 | Dyn5 | 10 | 1.18 | 0.1873 | 0.4 | 0.63 | 0 | 0 | -2 | 1.0794 | 2.5 | hv | FALSE | 2 | 4
63 MVA 110/20 kV | 150 | YNd5 | 110 | 22 | 0.04 | 20 | 63 | 0 | 0 | -9 | 0.32 | 1.5 | hv | FALSE | 9 | 18
100 MVA 220/110 kV | 0 | Yy0 | 220 | 55 | 0.06 | 110 | 100 | 0 | 0 | -9 | 0.26 | 1.5 | hv | FALSE | 9 | 12
25 MVA 110/10 kV | 150 | YNd5 | 110 | 14 | 0.07 | 10 | 25 | 0 | 0 | -9 | 0.41 | 1.5 | hv | FALSE | 9 | 12
40 MVA 110/20 kV | 150 | YNd5 | 110 | 18 | 0.05 | 20 | 40 | 0 | 0 | -9 | 0.34 | 1.5 | hv | FALSE | 9 | 16.2
40 MVA 110/10 kV v1.4.3 and older | 150 | YNd5 | 110 | 30.45 | 0.076 | 10 | 40 | 0 | 0 | -9 | 0.295 | 1.5 | hv | FALSE | 9 | 10.04
25 MVA 110/20 kV | 150 | YNd5 | 110 | 14 | 0.07 | 20 | 25 | 0 | 0 | -9 | 0.41 | 1.5 | hv | FALSE | 9 | 12
40 MVA 110/10 kV | 150 | YNd5 | 110 | 18 | 0.05 | 10 | 40 | 0 | 0 | -9 | 0.34 | 1.5 | hv | FALSE | 9 | 16.2

## trafo3w_std_types
| vector_group | vn_mv_kv | vn_lv_kv | shift_lv_degree | shift_mv_degree | pfe_kw | vn_hv_kv | i0_percent | sn_lv_mva | sn_hv_mva | sn_mv_mva | vkr_lv_percent | tap_neutral | tap_min | vk_mv_percent | vkr_hv_percent | vk_lv_percent | tap_max | vkr_mv_percent | tap_step_percent | tap_side | vk_hv_percent
63/25/38 MVA 110/10/10 kV | YN0yn0yn0 | 10 | 10 | 0 | 0 | 35 | 110 | 0.89 | 38 | 63 | 25 | 0.35 | 0 | -10 | 10.4 | 0.28 | 10.4 | 10 | 0.32 | 1.2 | hv | 10.4
63/25/38 MVA 110/20/10 kV | YN0yn0yn0 | 20 | 10 | 0 | 0 | 35 | 110 | 0.89 | 38 | 63 | 25 | 0.35 | 0 | -10 | 10.4 | 0.28 | 10.4 | 10 | 0.32 | 1.2 | hv | 10.4

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 1.06 | 0 | -215.6683 | 14.7853
1 | 1.045 | -4.6232 | -18.3 | -25.1575
2 | 1.01 | -12.1202 | 94.2 | -4.2836
3 | 1.0209 | -9.5553 | 47.8 | -3.9
4 | 1.0224 | -8.0731 | 7.6 | 1.6
5 | 1.07 | -12.6429 | 11.2 | 0.42749
6 | 1.0652 | -12.0158 | 0 | 0
7 | 1.09 | -12.0158 | 0 | -15.3434
8 | 1.0617 | -13.2881 | 29.5 | -4.8184
9 | 1.0558 | -13.4604 | 9 | 5.8
10 | 1.0594 | -13.1857 | 3.5 | 1.8
11 | 1.0576 | -13.3452 | 6.1 | 1.6
12 | 1.0562 | -13.3277 | 13.5 | 5.8
13 | 1.0593 | -13.3065 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 146.0229 | -17.8306 | -142.307 | 23.3265 | 3.7159 | 5.4959 | 0.59352 | 0.59016 | 0.59352 | 1.06 | 0 | 1.045 | -4.6232 | 1.4018
1 | 69.6454 | 3.0453 | -67.2967 | 1.3145 | 2.3487 | 4.3599 | 0.28126 | 0.28155 | 0.28155 | 1.06 | 0 | 1.0224 | -8.0731 | 0.66499
2 | 71.0265 | 3.7822 | -68.8393 | 0.80687 | 2.1872 | 4.589 | 0.29109 | 0.29151 | 0.29151 | 1.045 | -4.6232 | 1.01 | -12.1202 | 0.68851
3 | 51.8416 | -2.392 | -50.4113 | 3.1037 | 1.4303 | 0.71173 | 0.21239 | 0.21159 | 0.21239 | 1.045 | -4.6232 | 1.0209 | -9.5553 | 0.50164
4 | 37.7389 | 0.44081 | -36.9934 | -1.862 | 0.74558 | -1.4212 | 0.15446 | 0.15494 | 0.15494 | 1.045 | -4.6232 | 1.0224 | -8.0731 | 0.36594
5 | -25.3607 | 3.4768 | 25.7944 | -3.6897 | 0.43369 | -0.21292 | 0.10839 | 0.10916 | 0.10916 | 1.01 | -12.1202 | 1.0209 | -9.5553 | 0.25782
6 | -59.1025 | 15.8005 | 59.5819 | -14.2882 | 0.47945 | 1.5123 | 0.25629 | 0.25629 | 0.25629 | 1.0209 | -9.5553 | 1.0224 | -8.0731 | 0.60534
7 | 6.6209 | 2.5582 | -6.5791 | -2.4706 | 0.041795 | 0.087524 | 18.4129 | 18.4129 | 18.4129 | 1.07 | -12.6429 | 1.0594 | -13.1857 | 0.067006
8 | 6.4426 | 2.1229 | -6.3932 | -2.0201 | 0.049397 | 0.10281 | 17.5968 | 17.5968 | 17.5968 | 1.07 | -12.6429 | 1.0576 | -13.3452 | 0.064036
9 | 12.8447 | 4.8765 | -12.7357 | -4.6618 | 0.10907 | 0.21479 | 35.6415 | 35.6415 | 35.6415 | 1.07 | -12.6429 | 1.0562 | -13.3277 | 0.1297
10 | 5.9458 | 5.1931 | -5.9282 | -5.1464 | 0.017586 | 0.046715 | 20.6383 | 20.6383 | 20.6383 | 1.0617 | -13.2881 | 1.0558 | -13.4604 | 0.075104
11 | 0.47366 | 0.72274 | -0.47282 | -0.72095 | 0.00084196 | 0.001791 | 2.2591 | 2.2591 | 2.2591 | 1.0617 | -13.2881 | 1.0593 | -13.3065 | 0.0082209
12 | -3.0718 | -0.65364 | 3.0791 | 0.67064 | 0.0072596 | 0.016994 | 8.2565 | 8.2565 | 8.2565 | 1.0558 | -13.4604 | 1.0594 | -13.1857 | 0.030046
13 | 0.29316 | 0.42007 | -0.29264 | -0.4196 | 0.00051828 | 0.00046892 | 1.3444 | 1.3444 | 1.3444 | 1.0576 | -13.3452 | 1.0562 | -13.3277 | 0.0048925
14 | -0.47168 | -0.71864 | 0.47282 | 0.72095 | 0.0011322 | 0.0023052 | 2.2591 | 2.2591 | 2.2591 | 1.0562 | -13.3277 | 1.0593 | -13.3065 | 0.0082209

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 22.8263 | -10.1839 | -22.8263 | 11.383 | -3.5527e-15 | 1.1991 | 0.10471 | 0.9875 | 1.0209 | -9.5553 | 1.0652 | -12.0158 | 0.24732
1 | 13.0932 | -1.1307 | -13.0932 | 1.9962 | 5.3291e-15 | 0.86547 | 0.055055 | 34.6253 | 1.0209 | -9.5553 | 1.0617 | -13.2881 | 0.13003
2 | 37.1082 | 13.2357 | -37.1082 | -9.9851 | -1.4211e-14 | 3.2506 | 0.1648 | 99.6876 | 1.0224 | -8.0731 | 1.07 | -12.6429 | 0.38924
3 | -4.4409e-16 | -14.9943 | 8.8818e-16 | 15.3434 | 4.4409e-16 | 0.34904 | 0.5805 | 0.67726 | 1.0652 | -12.0158 | 1.09 | -12.0158 | 0.14219
4 | 22.8263 | 3.6114 | -22.8263 | -3.0936 | 0 | 0.51781 | 0.89471 | 60.2208 | 1.0652 | -12.0158 | 1.0617 | -13.2881 | 0.21915

## res_ext_grid
| p_mw | q_mvar
0 | 215.6683 | -14.7853

## res_load
| p_mw | q_mvar
0 | 21.7 | 12.7
1 | 94.2 | 19
2 | 47.8 | -3.9
3 | 7.6 | 1.6
4 | 11.2 | 7.5
5 | 29.5 | 16.6
6 | 9 | 5.8
7 | 3.5 | 1.8
8 | 6.1 | 1.6
9 | 13.5 | 5.8

## res_shunt
| p_mw | q_mvar | vm_pu
0 | 0 | -21.4184 | 1.0617

## res_gen
| p_mw | q_mvar | va_degree | vm_pu
0 | 40 | 37.8575 | -4.6232 | 1.045
1 | 0 | 23.2836 | -12.1202 | 1.01
2 | 0 | 7.0725 | -12.6429 | 1.07
3 | 0 | 15.3434 | -12.0158 | 1.09

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | bus | max_vm_pu | float64
6 | bus | min_vm_pu | float64
7 | bus | geo | object
8 | load | name | object
9 | load | bus | uint32
10 | load | p_mw | float64
11 | load | q_mvar | float64
12 | load | const_z_p_percent | float64
13 | load | const_z_q_percent | float64
14 | load | const_i_p_percent | float64
15 | load | const_i_q_percent | float64
16 | load | sn_mva | float64
17 | load | scaling | float64
18 | load | in_service | bool
19 | load | type | object
20 | load | controllable | bool
21 | gen | name | object
22 | gen | bus | uint32
23 | gen | p_mw | float64
24 | gen | vm_pu | float64
25 | gen | sn_mva | float64
26 | gen | min_q_mvar | float64
27 | gen | max_q_mvar | float64
28 | gen | scaling | float64
29 | gen | slack | bool
30 | gen | in_service | bool
31 | gen | slack_weight | float64
32 | gen | type | object
33 | gen | controllable | bool
34 | gen | max_p_mw | float64
35 | gen | min_p_mw | float64
36 | gen | id_q_capability_characteristic | Int64
37 | gen | reactive_capability_curve | bool
38 | gen | curve_style | object
39 | shunt | bus | uint32
40 | shunt | name | object
41 | shunt | q_mvar | float64
42 | shunt | p_mw | float64
43 | shunt | vn_kv | float64
44 | shunt | step | uint32
45 | shunt | max_step | uint32
46 | shunt | in_service | bool
47 | shunt | id_characteristic_table | Int64
48 | shunt | step_dependency_table | bool
49 | ext_grid | name | object
50 | ext_grid | bus | uint32
51 | ext_grid | vm_pu | float64
52 | ext_grid | va_degree | float64
53 | ext_grid | slack_weight | float64
54 | ext_grid | in_service | bool
55 | ext_grid | max_p_mw | float64
56 | ext_grid | min_p_mw | float64
57 | ext_grid | max_q_mvar | float64
58 | ext_grid | min_q_mvar | float64
59 | line | name | object
60 | line | std_type | object
61 | line | from_bus | uint32
62 | line | to_bus | uint32
63 | line | length_km | float64
64 | line | r_ohm_per_km | float64
65 | line | x_ohm_per_km | float64
66 | line | c_nf_per_km | float64
67 | line | g_us_per_km | float64
68 | line | max_i_ka | float64
69 | line | df | float64
70 | line | parallel | uint32
71 | line | type | object
72 | line | in_service | bool
73 | line | max_loading_percent | float64
74 | line | geo | object
75 | trafo | name | object
76 | trafo | std_type | object
77 | trafo | hv_bus | uint32
78 | trafo | lv_bus | uint32
79 | trafo | sn_mva | float64
80 | trafo | vn_hv_kv | float64
81 | trafo | vn_lv_kv | float64
82 | trafo | vk_percent | float64
83 | trafo | vkr_percent | float64
84 | trafo | pfe_kw | float64
85 | trafo | i0_percent | float64
86 | trafo | shift_degree | float64
87 | trafo | tap_side | object
88 | trafo | tap_neutral | float64
89 | trafo | tap_min | float64
90 | trafo | tap_max | float64
91 | trafo | tap_step_percent | float64
92 | trafo | tap_step_degree | float64
93 | trafo | tap_pos | float64
94 | trafo | parallel | uint32
95 | trafo | df | float64
96 | trafo | in_service | bool
97 | trafo | max_loading_percent | float64
98 | trafo | tap_changer_type | object
99 | poly_cost | element | uint32
100 | poly_cost | et | object
101 | poly_cost | cp0_eur | float64
102 | poly_cost | cp1_eur_per_mw | float64
103 | poly_cost | cp2_eur_per_mw2 | float64
104 | poly_cost | cq0_eur | float64
105 | poly_cost | cq1_eur_per_mvar | float64
106 | poly_cost | cq2_eur_per_mvar2 | float64
107 | res_bus | vm_pu | float64
108 | res_bus | va_degree | float64
109 | res_bus | p_mw | float64
110 | res_bus | q_mvar | float64
111 | res_line | p_from_mw | float64
112 | res_line | q_from_mvar | float64
113 | res_line | p_to_mw | float64
114 | res_line | q_to_mvar | float64
115 | res_line | pl_mw | float64
116 | res_line | ql_mvar | float64
117 | res_line | i_from_ka | float64
118 | res_line | i_to_ka | float64
119 | res_line | i_ka | float64
120 | res_line | vm_from_pu | float64
121 | res_line | va_from_degree | float64
122 | res_line | vm_to_pu | float64
123 | res_line | va_to_degree | float64
124 | res_line | loading_percent | float64
125 | res_trafo | p_hv_mw | float64
126 | res_trafo | q_hv_mvar | float64
127 | res_trafo | p_lv_mw | float64
128 | res_trafo | q_lv_mvar | float64
129 | res_trafo | pl_mw | float64
130 | res_trafo | ql_mvar | float64
131 | res_trafo | i_hv_ka | float64
132 | res_trafo | i_lv_ka | float64
133 | res_trafo | vm_hv_pu | float64
134 | res_trafo | va_hv_degree | float64
135 | res_trafo | vm_lv_pu | float64
136 | res_trafo | va_lv_degree | float64
137 | res_trafo | loading_percent | float64
138 | res_ext_grid | p_mw | float64
139 | res_ext_grid | q_mvar | float64
140 | res_load | p_mw | float64
141 | res_load | q_mvar | float64
142 | res_shunt | p_mw | float64
143 | res_shunt | q_mvar | float64
144 | res_shunt | vm_pu | float64
145 | res_gen | p_mw | float64
146 | res_gen | q_mvar | float64
147 | res_gen | va_degree | float64
148 | res_gen | vm_pu | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 3.2.2 | 3.2.0 | TRUE | FALSE |  | 60 | 100